## DFMEA
Production Item Name | Function Group | Function | Requirement | Potential Failure Mode | Potential Effects of Failure | Severity Rating: Failure Mode Effect | Potential Causes of Failure | Cause: Occurence Rating | Preventive Controls | Preventive Controls: Occurence Rating | Detective Controls | Detective Controls: Rating
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Conduct Required Current without Excessive Temperature Rise | Excessive temperature rise | Loss of power distribution function | 8 | Undersized cross-sectional area | 7 | Thermal modeling and sizing calculations | 3 | Thermal camera testing under load | 4
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Conduct Required Current without Excessive Temperature Rise | Localized overheating | Reduced current carrying capacity | 7 | Poor thermal dissipation design | 5 | Adequate heat sink integration | 4 | Heat dissipation tests | 4
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Conduct Required Current without Excessive Temperature Rise | Thermal deformation | Bus bar warpage | 7 | Inadequate material selection | 4 | Material selection per specification | 3 | Material certification inspection | 3
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Conduct Required Current without Excessive Temperature Rise | Insulation breakdown due to heat | Short circuit to adjacent components | 10 | Insulation with low temperature rating | 6 | Use of high temperature rated insulation | 3 | Insulation endurance test | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Conduct Required Current without Excessive Temperature Rise | Current derating | System operational limits exceeded | 8 | Incorrect current specification | 6 | Current rating verification during design | 4 | Current load tests | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Maintain Low Electrical Resistance | Increased contact resistance | Voltage drop across bus bar | 7 | Improper joining process | 5 | Process validation for joining methods | 3 | Micro-ohm resistance testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Maintain Low Electrical Resistance | Oxidation at joints | Heat generation at connection points | 7 | Exposure to air/moisture | 6 | Surface treatment/anti-oxidation coating | 3 | Visual inspection for oxidation | 4
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Maintain Low Electrical Resistance | Cold welds | Intermittent current flow | 6 | Inadequate welding parameters | 5 | Weld parameter verification | 3 | Destructive weld sample analysis | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Maintain Low Electrical Resistance | Loose connections | Arcing at connections | 8 | Improper torque on fasteners | 6 | Torque specification and training | 4 | Torque audit checks | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Maintain Low Electrical Resistance | Contaminant accumulation at interfaces | Reduced system efficiency | 6 | Lack of cleanliness during assembly | 5 | Clean room assembly protocol | 3 | Surface contamination testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Withstand Short Circuit Conditions | Thermal meltdown | System shutdown | 8 | Inadequate cross-sectional area for fault current | 6 | Short circuit analysis during design | 4 | Short circuit simulation tests | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Withstand Short Circuit Conditions | Mechanical deformation | Bus bar misalignment | 7 | Insufficient mechanical support | 5 | Reinforced mounting and supports | 4 | Mechanical load testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Withstand Short Circuit Conditions | Joint separation | Loss of electrical continuity | 8 | Weak joint design | 5 | Joint design review | 3 | Joint pull tests | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Withstand Short Circuit Conditions | Weld cracking | Formation of hot spots | 7 | Poor weld quality | 5 | Weld quality standards | 3 | Weld x-ray inspection | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Withstand Short Circuit Conditions | Loss of system integrity | Electrical fire risk | 10 | Improper fault current calculation | 6 | Protective device coordination study | 3 | Protective device functional test | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Meet Clearance and Creepage Distances | Insufficient clearance between phases | Short circuit between phases | 10 | Design errors in spacing | 6 | CAD review for clearance compliance | 3 | Dielectric strength testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Meet Clearance and Creepage Distances | Reduced creepage path | Loss of electrical isolation | 8 | Improper mounting or assembly | 5 | Assembly fixture control | 3 | Assembly inspection | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Meet Clearance and Creepage Distances | Dielectric breakdown | Bus bar surface carbonization | 7 | Environmental contamination | 6 | Environmental protection measures | 4 | Surface contamination testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Meet Clearance and Creepage Distances | Arcing across bus bar gaps | Electrical fire | 10 | Wear of insulating materials | 5 | Upgrade insulation materials | 4 | Insulation resistance measurement | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Meet Clearance and Creepage Distances | Contaminant bridging | Unintended current paths | 8 | Incorrect bus bar geometry | 6 | Design verification checklist | 3 | Dimensional inspection | 4
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Structural Integrity under Mechanical Loads | Bus bar bending | Loss of alignment | 7 | Insufficient material thickness | 5 | Structural FEA analysis | 3 | Mechanical load testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Structural Integrity under Mechanical Loads | Cracking at mounting points | Mechanical failure | 8 | Sharp corners/stress risers | 6 | Fillet and radius design | 3 | Visual inspection for cracks | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Structural Integrity under Mechanical Loads | Fatigue under vibration | Electrical continuity loss | 8 | Lack of vibration damping | 5 | Vibration isolation in mounting | 3 | Vibration testing | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Structural Integrity under Mechanical Loads | Mounting bolt loosening | System vibration-induced faults | 7 | Incorrect torque application | 6 | Torque specification and training | 4 | Torque audit | 5
Bus Bar | Electrical Power Distribution | Electrical Power Distribution | Structural Integrity under Mechanical Loads | Detachment from supports | Complete bus bar separation | 8 | Weak support design | 5 | Support bracket design review | 3 | Mounting integrity check | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Insulate Bus Bar from Adjacent Conductors and Ground | Insulation cracking | Short circuit to ground | 10 | Mechanical stress during assembly | 6 | Proper handling procedures | 3 | Hi-pot testing | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Insulate Bus Bar from Adjacent Conductors and Ground | Insulation abrasion | Inter-phase short circuit | 10 | Contact with sharp edges | 5 | Edge deburring and rounding | 3 | Visual inspection | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Insulate Bus Bar from Adjacent Conductors and Ground | Insulation displacement | Exposure of live parts | 8 | Improper insulation application | 6 | Process validation for insulation | 3 | Insulation coverage check | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Insulate Bus Bar from Adjacent Conductors and Ground | Pinholes/voids in insulation | Electrical tracking | 7 | Manufacturing defects | 5 | In-process inspection | 3 | Ultrasound void detection | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Insulate Bus Bar from Adjacent Conductors and Ground | Insulation thermal aging | Reduced dielectric strength | 8 | High operating temperatures | 6 | Thermal performance validation | 4 | Thermal aging tests | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Provide Sufficient Environmental Protection | Water ingress | Bus bar corrosion | 7 | Inadequate enclosure sealing | 6 | Seal design review | 3 | Ingress protection (IP) testing | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Provide Sufficient Environmental Protection | Corrosive gas attack | Reduced electrical performance | 8 | Installation in harsh environment | 5 | Material selection validation | 3 | Corrosion chamber testing | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Provide Sufficient Environmental Protection | Dust accumulation | Contamination-induced shorts | 7 | Improper dust filter placement | 6 | Dust filter design review | 3 | Visual inspection for dust | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Provide Sufficient Environmental Protection | UV degradation | Aging and cracking | 6 | Lack of UV resistant materials | 6 | UV resistance qualification | 3 | Accelerated weathering tests | 5
Bus Bar | Electrical Insulation and Protection | Electrical Insulation and Protection | Provide Sufficient Environmental Protection | Coating delamination | Insulation compromise | 7 | Incorrect coating process | 5 | Coating process control | 3 | Coating adhesion test | 5